## Case details
Energy Memo: GLA Consultation
Case details
Date of first review: | 2020-01-17
Case Name: | Hampton Pool
Case Number: | 4750
Case Officer: | Reece Harris
London Borough: | Richmond
Application Type (Outline/Hybrid/Detailed): | Detailed
Applicant: | London Borough of Richmond
Energy Consultant: | Max Fordham
Document Title: | Energy Strategy
Document Date: | Decemeber 2019
Development proposals
Use | Floorspace/Number of units
D2/A2 | 1789 m2
m2
m2

## Pre-application advice
Paste pre-application comments here for reference, if available.

## Energy Comments
Comment No. | GLA Post Stage I | Applicant's Post Stage I response
| Date: 17/01/2020 | Date:
General compliance comments
1 | The Energy Hierarchy has been followed; the proposed strategy is generally supported; however, the applicant should submit additional information to ensure compliance with the London Plan policies. | This is still oustanding. | Refer to the "London" section within "Policy Context" in the report. (Section 2.2.)
2 | For the purposes of this assessment, the applicant will be estimating the CO2 emission performance against London Plan policies using the SAP 10 emissions factors. This is supported. | Nothing further required. | good
3 | The applicant has submitted the GLA’s Carbon Emission Reporting spreadsheet, which has been developed to allow the use of the updated SAP 10 emission factors alongside the SAP 2012 emission factors. | Nothing further required. | good
Be Lean
5 | Based on the information provided, the non-domestic element of the proposed development does not appear to achieve any carbon savings from energy efficiency alone compared to a 2013 Building Regulations compliant development. The applicant should note that the new draft London Plan includes a target of a 15% improvement on 2013 Building Regulations from energy efficiency which applicants should be aiming towards. The applicant should therefore model investigate energy efficiency measures and aspire to meet the EE target. It is noted that all energy loads have been improved for the development with the exception of the hot water load. The solar hot water has not been accounted for within the calculations; however, this is considered a renewable technology and any savings associated with this technology, if accounted, would be catagorised under the Be Green section of the hierarchy. The applicant should investigate the use of waste water heat recovery systems with the shower waste water. | This is still oustanding. | Refer to Section 1.1. - Executive Summary: The London Plan states that “if the extension is > 25% of the total useful floor area of the existing development then the CO2 saving for the development as a whole should be calculated relative to the Part L 2013 Baseline”. Therefore the refurbished building is essentially benchmarked against a new build. Given that over 50% of the building volume is refurbished to be reused, it is not possible to achieve 15% better than the baseline in the Be Lean section of the hierarchy. This shortfall is clearly presented in the report with the overall carbon reduction shown to later exceed the overall 35% minimum requirement and the Be Green stage. The development suggests that this is a practical approach for dealing with a refurbishment of this scale that already contains the existing building. Refer to Energy Memo - Stage I consultation - 30/05/2019 - Hampton Swimming Baths, section6 The applicant should therefore model additional energy efficiency measures and at a minimum commit to the development exceeding 2013 Building Regulations compliance through energy efficiency alone. As presented the design is already highly aspirational in is low energy design. It proposes: high efficiency lighting, MVHR, high efficiency cooling, high spec pump / controls and passive design elements (solar shading and natural ventilation). It showcases very high performance fabric in areas of new build which are considerably better than Part L U-values, and commits to updating / refurbishing elements of existing fabric. Given that over 50% of the floor area is an existing building with poor thermally performing fabric, the combination of these interventions is able to push the buildling up to compliance with the existing Building Regs (2013). Further fabric improvements on the "Be Lean" model are impractical without rebuilding much of the existing structure - given primary energy cost and monetary cost to this we instead suggest an approach that improves the fabric as much as is practical, and then supplements the shortfall with high performance technology in the Be Green stage. It is recognised that there could potential for integrating waste water heat recovery into the design. Practically, it will depend on constraints such as the available floor to ceiling height and existing ground foundations in the shower area, and the ability to integrate the heat recovery circuit with the proposed mechanical assembly. It is suggested that a note on integrating waste water heating, along with a description of the solar thermal integration (see later) is requested as a planning condition to be submitted at a later date when a more detailed design has been developed.
Overheating
8 | The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building has been provided and the applicant has demonstrated that the actual building’s cooling demand is lower than the notional. For the naturally ventilated spaces, a Dynamic Overheating Analysis has been undertaken using the CIBSE TM52 methodology. Its results demonstrate that DSY 1 compliance is achieved for all spaces and DSY 2 and 3 compiance is achieved for most spaces. Those areas that do not comply under the DSY 2 and 3 scenarios have a retrofit strategy for increased mechnical ventialtion to be installed in future if required. |  | good.
Be Clean
9 | The applicant has carried out an investigation and there are no existing or planned district heating networks within the vicinity of the proposed development. | Nothing further required. | good.
10 | The applicant has provided a commitment to ensure that the development is designed to allow future connection to a district heating network. Schematics on how this can be achieve has been provided. | Nothing further required. | good.
11 | The applicant is proposing a communal heat network supplied by a centralised energy centre. A drawing indicating the floor area, internal layout and location of the energy centre has been provided. | Nothing further required. | good.
Be Green
13 | The applicant is proposing to install 36.5 kWp of Photovoltaic (PV and PV-T) panels equating to circa 375 m2 of net PV area and 44,459 kWh of electricity generation. A detailed roof layout has been provided demonstrating that the roof’s potential for a PV installation has been maximised. The on-site savings from renewable energy technologies should be maximised regardless of the London Plan targets having been met. To accurately report the PV-T savings can the applicant revise the Be Green hot water demands witihn the GLA carbon emission reporting spreadsheet to demonstrate the saving achieved by the solar hot water output. | This is still oustanding. | The design team see's the intergration of PV-T into the scheme to be a potentially high value intervention given the high domestic hot water load on the site. That said, PV-T is a relatively young technology whose benefits cannot be easily modelled using today's compliant methodologies; in addition the effectiveness of a PV-T panel also depends on detailed system configuration which has not been fully developed at this early stage in the project. For these reasons, the energy strategy presented assumes no positive benefit from the solar thermal contribution of the PV-T panels, modelling only the PV element of the electrical generation. When modelled as described the scheme is able to achieve better than the minimum requirements stipulated by the London Plan (i.e. 35% reduction compared to Part L Regs). As such, the scheme is committing to achieve the electrical generation modelled here, but is not committing to incorporating the solar thermal element associated to PV-T panels at this stage. As the design develops the design team will continue to assess the practical suitability of incorporating PV-T on the site, but the current modelling reserves the option to swap the PV-T panels for better performing electrical only PV panels (i.e. the as presented strategy), should PV-T be deemed impractical, which will actually improve the current Be Green energy reduction on those currently presented in the report.
14 | Centralised heat pumps are being proposed in the form of a ASHP gas boiler and WSHP system. Further information on the heat pumps should be provided including: a. An estimate of the heating energy (MWh/annum) the heat pumps would provide to the development and the percentage of contribution to the site’s heat loads. | This is still oustanding. | The following metrics have been extracted from the modelling presented: Annual Space Heating Load (MWHr/yr) = 32.8 Annual Domestic Hot Water Load (MWHr/yr) = 256.5 Total Annual Heat Load (MWHr/yr) = 289.3 Space Heating Load delivered by ASHP (MWHr/yr) = 32.8 Domestic Hot Water Load delivered by ASHP (MWHr/yr) = 163.2 Domestic Hot Water Load delivered by WSHP (MWHr/yr) = 93.3 ASHP contribution to total heat load (ratio) = 0.68 WSHP contribution to total heat load (ratio) = 0.32 It is noted that new boilers will be installed on the site. These will deliver the majority of the unregulated swimming pool heating load as well as providing plant redundancy to the main regulated heating system.
Carbon performance and offsetting
16 | The carbon dioxide savings exceed the on-site target set within Policy 5.2 of the London Plan for non-domestic uses. The appicant is require to respond to all outstanding items. | This is still oustanding. | Good. Our view is that the latest energy report responds to all GLA Stage 1 comments. The presented design delivers a building that achieves Part L Building Regulations in the Be Lean stage of the design (referencing previous guidance from the Energy Memo - Stage I consultation - 30/05/2019), despite being majority existing fabric with poor thermal performance. It also delivers greater savings than requried within the Be Green stage of the design by integrating heat pumps maximising PV potential on the roof. There are aspirations to further explore whether it is practical to incorporate solar thermal capture from PV-T panels, as well as waste water heat recovery into the domestic hot water heating system. Currently compliant modelling methodologies are not able to model waste water heat recovery or PV-T / water source heat pump systems. To be able to more accurately asses the associated improvement in performance will require a more detailed look at the system configuration, which will happen in the next phase of design. It is suggested that a design note is required at a later stage, that conditions performance at least as good as is presented here and requires a more detailed explanation of the mechanical arrangement. please note. waste water heat recovery and PV-T incorporated into a water source heat pump domestic hot water system are innovative approaches. while it is the aspiration of the project to make use of these technologies they need to be considered in detail before fully committing to this approach.
Other points
Move resolved comments under this section

## CO2 performance
Domestic
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations
Energy Efficiency |  | 0 | #DIV/0!
CHP |  | 0 | #DIV/0!
Renewable energy |  | 0 | #DIV/0!
Total |  | 0 | #DIV/0!
Non-domestic
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 80
Energy Efficiency | 82 | -2 | -2.5%
CHP | 82 | 0 | 0%
Renewable energy | 40 | 42 | 52.5%
Total |  | 40 | 50%
Carbon offsetting
| Shortfall (tonnes per annum) | Shortfall (£)
Domestic
Non-domestic
Total